SJ

HANDOUK

►FEATURES

| ● 4000V dielectric strength ● Photo isolation ● Built-in snubber ● Zero cross or random turn-on ● TRIAC AC output ● Panel mount ● DC or AC control | ● With LED indicator or not ● Environmental protection product available (RoHs compliant) ● Size (LxWxH) : 58.4 x 45.7 x 22.9mm ● E197546 |
| --- | --- |

►description

The SJ offer 3-32VDC, 110VAC, or 220VAC input control, with outputs rated at 10,15,20,25 or 40Amps. 
All models include an internal snubber. The relays provide 4000Vrms optoisolation, between input and output. Outline dimension is 58.4 x 45.7 x 22.9mm.

►INPUT

| Control voltage range (DC input) | 3 to 32VDC |
| --- | --- |
| Control voltage range (AC input) | 85 to 132VAC (110V input) 175 to 264VAC (220V input) |
| Must operate voltage (DC input) | Max. 3 VDC |
| Must operate voltage (AC input) | 85VAC (110V input) 175VAC (220V input) |
| Must release voltage (DC input) | Min. 1.0VDC |
| Must release voltage (AC input) | 10VAC |
| Maximum input current (DC input) | 25mA (at 32VDC) |
| Maximum reverse protection voltage (DC input) | -32VDC |

►OUTPUT

| Type (SJ- D□□□) | D□□10 | D□□15 | D□□20 | D□□25 | D□□40 |
| --- | --- | --- | --- | --- | --- |
| Load Voltage range(at 47-63HZ) | D240 48 to 280Vrms |  |  |  |  |
|  | D380 48 to 400Vrms |  |  |  |  |
| Transient over voltage | D240 600Vpk |  |  |  |  |
|  | D380 800Vpk |  |  |  |  |
| Load current range(A) | 0.1 to 10 | 0.1 to 15 | 0.1 to 20 | 0.1 to 25 | 0.1 to 40 |
| Max. surge current(10ms) | 100Vpk | 150Vpk | 200Vpk | 250Vpk | 400Vpk |
| Max. leakage current | 5mA | 5mA | 5mA | 5mA | 5mA |
| Max. on-state voltage drop | 1.5VAC |  |  |  |  |
| Max. turn-on time | 1/2 cycle + 1ms (Zero cross) |  |  |  |  |
| Max. turn-on time | 1ms (Random turn-on) |  |  |  |  |
| Max. turn-on time | 1/2 cycle + 1ms |  |  |  |  |
| Min. off-state(dv/dt) | 200V / µS |  |  |  |  |
| Min. power factor | 0.5 |  |  |  |  |

►GENERAL

| Type (SJ- D□□□) |  | D□□10 | D□□15 | D□□20 | D□□25 | D□□40 |
| --- | --- | --- | --- | --- | --- | --- |
| Dielectric strength ( input to output ) |  | 4000VAC (50/60 Hz, 1 min.) |  |  |  |  |
| Insulation resistance |  | 1000MΩ (50/60 Hz, 1 min.) |  |  |  |  |
| Ambient temperature | Operating | -30°C to +80°C |  |  |  |  |
|  | Storage | -30°C to +100°C |  |  |  |  |
| Unit weight |  | Typically 88g |  |  |  |  |

►ORDERING INFORMATION

►Precautions

- When choosing a SSR, please notice the actual load current and working ambient 
temperature. To use the SSR correctly, please refer to CHARACTERISTICS DATA 
and make sure the heat sink size when it works in full load current.

- Apply heat-radiation silicon grease of heat conductive sheet between the SSR and heat sink. There will be a space between the SSR and heat sink Attached to the SSR. Therefore, the generated heat of the SSR cannot be radiated properly without the grease. As a result, the SSR may be overheated and damaged or deteriorated.

- Tighten the SSR terminal screws properly. If the screws are not tight, the SSR will be damaged by heat generated when the power in ON. Perform wiring using the tightening torque shown in the following table.

| Screw size | Recommended tightened torque |
| --- | --- |
| M3 | 0.58 to 0.98 N·m |
| M4 | 0.98 to 1.37 N·m |

►dimensions (Unit: mm)

►CHARACTERISTICS CURVE