Sheet 1 of  5

The Littelfuse Industrial iTMOV 34S Series thermally protected varistor represents a new development in circuit protection. It consists of a 34mm square format varistor element ( MOV) with an integral thermally activated element designed to open in the event of overheating due to abnormal

over-voltage, limited current conditions.

The device has a third lead, an indicator lead, which may be used to indicate that the MOV has been disconnected from the circuit. This lead facilitates connection to monitoring circuitry.

The iTMOV 34S devices offer quick thermal response due to the close proximity of the integrated thermal element to the MOV body. The integrated configuration also offers lower inductance than most discreet solutions resulting in improved clamping performance to fast over-voltage transients.

Features:

US Patent for Thermally Protected  MOV

-   Patent # 6636403

Designed to facilitate compliance to UL1449

for TVSS   product.

Hi Peak Current Rating to 40 kA.

-55 Deg C  to +85 Deg C operating temp.

Agency Recognition Pending:   UL    CSA

Alternative Design available with

narrow 3mm wide monitor ( right) lead.

Absolute Maximum Ratings.:

Continuous:

Steady State Applied Voltage:				          UNITS

AC Voltage Range (VM(AC)RMS)…………………………………………………	115 	  to    750		V

Transient:

Peak Pulse Current (ITM)

For 8/20µs Current Wave, single pulse..……………………………………..	                                       up to      	 40000		A

Single Pulse Energy Capability

For 2ms Current Wave……………………………………………………….…	235   	to    1050		J

Operating Ambient Temperature range (TA)…………………………………………..	-55	 to 	+85	ºC

Storage Temperature (TSTG)…………………………………………………………….	-55	 to 	+125	ºC

Temperature Coefficient (V) of Clamping Voltage (VC) at Specified Test Current	<0.01			%/ºC

Hi-Pot Encapsulation (Isolation Voltage Capability)………………………………….	     2500			V

Thermal Protection Isolation Voltage Capability (when operated)

- Under UL 1449 Limited Current Test Procedure -  see Note #1....………..	600			V

Insulation Resistance…………………………………………………………………….	1000			M

Notes-

#1  -  Under Ul1449 limited current testing parts rated >420V will not open due

to 600V voltage limit. Devices with ratings >420V have not yet been evaluated.

CAUTION: Stresses above those listed in “Absolute Maximum Ratings” may cause permanent damage to the device. This is a stress only rating and operation of the device at these or other conditions above those indicated in the operational sections of this specification is not implied.

Ratings, Specifications

and Dimensions as shown are subject to change.

Sheet 2 of 5

Device Ratings and Specifications:

Table #1:

|  | MAXIMUM RATING (85°C) |  |  |  |  | SPECIFICATIONS (25°C) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CONTINUOUS |  |  | TRANSIENT |  | VARISTOR VOLTAGE AT 1mA TEST CURRENT |  | MAXIMUM CLAMPING VOLTAGE 8/20µs at 200A | TYPICAL CAPACI-TANCE f = 1MHz |
|  | AC VOLTS | DC VOLTS | MCOV SURGE ARRESTER 85% of std rating | ENERGY 2ms | PEAK SURGE CURRENT 8/20µs |  |  |  |  |
|  | VM(AC)RMS | VM(DC) | VM(AC)RMS | WTM 1 x PULSE | ITM 1 x PULSE | VN(DC) MIN | VN(DC) MAX | VC | C |
|  | (V) | (V) | (V) | (J) | (A) | (V) |  | (V) | (pF) |
| TMOV34S111M | 115 | 150 | 97.75 | 235 | 400001 | 163 | 202 | 305 | 11500 |
| TMOV34S131M | 130 | 175 | 110.5 | 270 | 400002 | 184 | 228 | 345 | 10000 |
| TMOV34S141M | 140 | 188 | 119 | 291 | 400003 | 198 | 248 | 375 | 9000 |
| TMOV34S151M | 150 | 200 | 127.5 | 300 | 400004 | 212 | 268 | 405 | 8000 |
| TMOV34S181M | 180 | 240 | 153 | 330 | 400005 | 254 | 312 | 488 | 6800 |
| TMOV34S201M | 200 | 265 | 170 | 335 | 40000 | 283 | 357 | 540 | 6500 |
| TMOV34S251M | 250 | 330 | 212.5 | 370 | 40000 | 354 | 429 | 650 | 5000 |
| TMOV34S271M | 275 | 369 | 233.75 | 400 | 40000 | 389 | 473 | 730 | 4500 |
| TMOV34S301M | 300 | 400 | 255 | 435 | 40000 | 433 | 528 | 780 | 4050 |
| TMOV34S321M | 320 | 420 | 272 | 460 | 40000 | 462 | 561 | 830 | 3800 |
| TMOV34S331M | 330 | 435 | 280.5 | 475 | 40000 | 476 | 581 | 855 | 3700 |
| TMOV34S351M | 350 | 460 | 297.5 | 500 | 40000 | 505 | 616 | 910 | 3500 |
| TMOV34S391M | 385 | 506 | 327.25 | 550 | 40000 | 555 | 678 | 1005 | 3300 |
| TMOV34S421M6 | 420 | 560 | 357 | 600 | 40000 | 610 | 748 | 1130 | 3000 |
| TMOV34S461M6 | 460 | 610 | 391 | 620 | 40000 | 642 | 783 | 1188 | 2800 |
| TMOV34S481M6 | 480 | 640 | 408 | 650 | 40000 | 670 | 825 | 1240 | 2700 |
| TMOV34S511M6 | 510 | 675 | 433.5 | 700 | 40000 | 735 | 910 | 1350 | 2500 |
| TMOV34S551M6 | 550 | 700 | 467.5 | 735 | 40000 | 770 | 939 | 1415 | 2250 |
| TMOV34S571M6 | 575 | 730 | 488.75 | 770 | 40000 | 805 | 1000 | 1480 | 2200 |
| TMOV34S621M6 | 620 | 800 | 527 | 840 | 40000 | 880 | 1074 | 1589 | 2100 |
| TMOV34S661M6 | 660 | 850 | 561 | 900 | 40000 | 940 | 1160 | 1720 | 2000 |
| TMOV34S681M6 | 680 | 890 | 578 | 950 | 40000 | 980 | 1195 | 1772 | 1970 |
| TMOV34S751M6 | 750 | 970 | 637.5 | 1050 | 40000 | 1080 | 1320 | 2000 | 1800 |

Notes

- Peak current applies to applications rated up to 100V AC rms,  132V DC. Peak current is 30kA max for applications greater than 100V AC rms, 132 V DC.

- Peak current applies to applications rated up to 115V AC rms., 145V DC. Peak current is 30kA max for applications greater than 115V AC Vrms, 145 V DC.

- Peak current applies to applications rated up to 123 V AC rms., 165V DC. Peak current is 30kA max for applications greater than 123V AC Vrms, 165 V DC.

- Peak current applies to applications rated up to 132V AC rms, 176 V DC. Peak current is 30kA max for applications greater than 132V  AC Vrms, 176V DC.

- Peak current applies to applications rated up to 158V AC rms, 211 V DC. Peak current is 30kA max for applications greater  than  158V  AC Vrms, 211V DC.

6.	Devices with ratings >420V have not yet been evaluated.

For Power Dissipation Ratings, VI Curve, and Pulse Rating Curves

see Littelfuse HB Series Data Sheet.

All Ratings, Specifications

and Dimensions as shown are preliminary and subject to change.

Sheet 3  of 5

Note-

To Order Alternative Design with narrow 3mm monitor lead (right hand terminal as shown)

add suffix X2696 to part number.

See Table of Dimensions on next page.

Sheet 4  of 5

Table  # 2 :  Dimensions in mm

| Part Number | T max Body Thickness | S Mounting Terminal Offset |
| --- | --- | --- |
| TMOV34S111M | 11.9 | 5.2 ±.65 |
| TMOV34S131M | 12.2 | 5.5 ±.65 |
| TMOV34S141M | 12.3 | 5.7 ±0.85 |
| TMOV34S151M | 12.4 | 5.9 ±0.85 |
| TMOV34S181M | 12.8 | 6.3 ±0.85 |
| TMOV34S201M | 13.0 | 6.5 ±0.85 |
| TMOV34S251M | 11.8 | 6.25 ±0.85 |
| TMOV34S271M | 12.0 | 6.5 ±0.85 |
| TMOV34S301M | 12.3 | 6.8 ±1.0 |
| TMOV34S321M | 12.5 | 6.9 ±1.0 |
| TMOV34S331M | 13.0 | 7.2 ±1.0 |
| TMOV34S351M | 13.1 | 7.4 ±1.0 |
| TMOV34S391M | 13.2 | 7.6 ±1.0 |
| TMOV34S421M | 13.4 | 7.85 ±1.0 |
| TMOV34S461M | 13.7 | 8.15 ±1.0 |
| TMOV34S481M | 13.9 | 8.25 ±1.0 |
| TMOV34S511M | 14.2 | 8.6 ±1.0 |
| TMOV34S551M | 14.8 | 8.65 ±1.0 |
| TMOV34S571M | 15.0 | 8.85 ±1.0 |
| TMOV34S621M | 15.4 | 9.25 ±1.0 |
| TMOV34S661M | 15.8 | 9.65 ±1.0 |
| TMOV34S681M | 16.0 | 9.85 ±1.0 |
| TMOV34S751M | 16.3 | 10.65 ±1.0 |

Ratings, Specifications and Dimensions as shown

are preliminary and subject to change.

Sheet 5  of 5

Line

Line Fuse

Neutral

Diode

LED

R

Normally On

To Protected Circuit

TMOV34S

TMOV34S series devices have third lead ( as indicated  in drawing on sheet #3 ) to facilitate connection to monitoring circuit.

This will indicate if varistor has been disconnected from protected circuit.

See typical arrangement below.